CAÑON CITY AREA FIRE PROTECTION DISTRICT

1475 North 15th Street

Cañon City CO 81212

719-275-8666/FAX 719-275-1486

Cistern/Dry Hydrant Permit Application

Date:

Project:

Address of project:

Contractor: 								E-Mail:			Phone:

Address:

Contact person:							E-Mail:			Phone:

FAX Number

The following items MUST be included within the documents submitted for review.  Plans will not be reviewed unless all items are included.  Confirm each item below is included.

- Full size, scalable site plan indicating proposed cistern and dry hydrant(s) location

- Project Address Shown on Plans

- Cistern design plans indicating all piping (vent, fill, suction, etc.) water level indicators, anti-vortex, capacity, man-ways etc.

- Dry hydrant design, pipe size and length

- Refer to Cistern/Dry Hydrant Requirement form

Signature:											Date:

Name Printed:

Fee Submitted:						(See fee schedule)		Date:

Plans will not be reviewed until fee(s) submitted

Office use only

Accepted by:										Date:

CAÑON CITY AREA FIRE PROTECTION DISTRICT

Cistern and Dry Hydrant Requirements

- Cistern size will be determined using NFPA 1142 with no reductions for area separation.

- A scalable site plan indicating the location of the cistern and hydrant(s) is required.

- Cistern design plans, NFPA 22, indicating all piping (vent, fill, suction, etc. ), water level indicators, anti-vortex, capacity, man-ways etc. must be submitted and approved before installation of the cistern.

- Usable capacity of cistern shall be the number of gallons above the level of the anti-vortex plate.

- An anti-vortex plate will be required at the entrance of the suction piping.

- Maximum lift of 11' measured from the anti-vortex plate to the center line of the dry hydrant.

- Cistern and dry hydrant(s) must be approved, installed and tested before construction unless approved.

- Cistern will be for fire service use only and not used for any other purpose unless approved.

- Cistern must be maintained full at all times, with an approved and accessible means for verifying full water level.

- Piping and venting of cistern shall be adequate to supply a minimum of 1000 GPM.

- Piping between cistern and hydrants must be flushed using approved methods.

- The cistern shall be connected to a/an dry hydrant(s) capable of the required fire flow for the proposed building(s).  The minimum flow rate shall be 1000 GPM as measured from a draft.

- Dry hydrant(s) shall be protected from freezing, protected from vehicle damage and be within 5' of  fire apparatus access.  Connection for the apparatus shall be 6" NST male threads with a protective cap.  The connection shall be 40" at the centerline above apparatus access road.

- Typical fire hydrants used as dry hydrants shall have (2) 2 1/2" and (1) 5"outlets.  The 5" outlet shall be adapted to 6" male thread with a protective cap.  All threads shall be NST.  Typical hydrants shall have a permanent sign attached indicating "For Draft Only".

- Cisterns of 30,000 gallons or more may qualify for ISO rating reduction for all structures within 1,000 feet of cistern.